## Lot.5
لست تجهیزات مورد ضرورت سب ستیشن های مرکز و ولایات بابت پلان تدارکاتی سال 1402 هـ.ش - Lot . 5
شماره | حوزه | ولایت | سب ستشن | وسایل وتجهیزات مورد ضرورت | مشخصات تخنیکی | کمپنی مربوطه | واحد | مقدار | قیمت فی واحد به (افغانی) | قیمت مجموعی (افغانی) | تصویر کتلاک تجهیزات | ملاحظات
1 | كابل | كابل | چمتله | پول سرکیت بریکرگازی 245KV SF6 complete Pole for Circuit Breaker 245kv-Type:200SFM-40S. | Complete pole Unit With all accessuriese Without Wired Housing Structure & Mechanism of 245 Kv Circuit Breaker , Type: (200SFM-40S - Serial No- X300261) - Outdoor. STD - IEC 62271 - 100 , Rated Voltage-245kv, Rated Short Cicuit Making current - 100 kAp , rated frequency 50HZ , First pole to clear Factor - 1.3 , Creepage Distance(Total) - 6125 mm, | Crompton Greaves limited | Set( pole without Mechanism ) | 3
Rated operating sequence ( 0 - 0.3 sec - CO - 3 MIN - CO ) , Rated lightning impulse with stand voltage - 1050 kVp, Number of tripping coil 2 , Protection Class IP55 , Number of pole 3 ,Type of Machanism - Spring-Spring , Rated Current-1600A, Rated SF6 gas pressure 7 kg/cm2 -at20c,
2 | کابل | کابل | سب ستیشن چمتله | لایتننګ ارستر 110kv | 110kv Lightning Arrester.Outdoor type Metovar Metal oxide Surge Arrester for 110kV system Voltage. Rated Voltage – 96 kv….Include -( Bottom – 48 kv and Top – 48kv). Discharge Current – 10 kA. Rated Frequency – 50 Hz. L.D. Discharge Class – 2. Pressure Relief Class – 40 kA (RMS). M.C.O.V. – 81 kv., Protection Class IP55 , Model ZAQ-96-SM, STD: IEC 60099 - 6 | Indian or Equivalent | Nos | 3 |  |  |  | این قلم میتواند مطابق به مشخصات برقی از کمپنی مربوطه و یا هر کمپنی دیگر تهیه گردد.
3 | كابل | كابل | سب ستیشن چمتله | لایتننګ ارستر 20kv | Lightning Arrester for 20kv system. 1- Rating – 20kv -10kA 2- P.R Class – 40. kA (RMS). 3- Frequency – 50 HZ. 4- L.D. Class – 2. 5- M.C.O.V – 16 kV (RMS). Protection Class IP 55 outdoor Installation, model ZAB-20-SM, STD: IEC 60099 - 6 | Indian or Equivalent | Nos | 15 |  |  |  | این قلم میتواند مطابق به مشخصات برقی از کمپنی مربوطه و یا هر کمپنی دیگر تهیه گردد.
4 | بلخ | بلخ | نائب آباد | سرکت بریکرگازی 220KV SF6 هوای ازاد | GAS CIRCUIT BREAKER TYPE: 200-SFM-40S RATED LIGHTING IMPULSE WITHSTAND VOLTAGE 1050KVP RATED SHORT.CIRCUIT BREAKING CURRENT 40KA FIRST POLE TO CLEAR FACTOR 1.5 MOTORVOLTAGE 110VDC RATED DURATION OF SHORT CIRCUIT CURRENT 40KA/3SEC RATED LINE CHARGING BREAKING CURRENT 125A GAS WT 21KG SR. NO. 22512C RATED VOLTAGE 245KV RATED FREQUENCY 50HZ RATED NORMAL CURRENT 1250A RATED COLOSING VOLTAGE 110V.DC RATED SF6 GAS PRESSURE 7 Kg / cm2 - g ( AT 20 C ) RATED VOLTAGE AND FREQUENCY FOR AUX. CIRCUIT 1 Ø 230 VAC . 50 Hz TOTAL WT. WITH GAS3900KG RATED OPERATING SEQUENCE 0 - 0.3SEC - CO - 3 MIN - CO YEAR OF MFG 2006 STD.IEC 62271 - 100 | Crompton Greaves limited | سیت ( میکانیزم معۀ پُل کنکت برای یک فاز) | 1
5 | بلخ | بلخ | نائب آباد | Line Distance Relay D60 | Ratings: Control Power:125-250V, 0.7A/100 , 50/60HZ ,0.7A, Contact Inputs: 300V, Max 10mA | sel | Nos | 1
6 | بلخ | فاریاب | شیرین تگاب | PT For 110KV | TYPE:IVT 123/550, Highest system voltage:123kV, Voltage factor:1.2Cont/1.5-3sec, Creepage Distance: 3075mm, Altitude:>1000meter, insulation level: 230 / 550kV | Crompton Greaves limited | Nos | 2
A - N 1a - 1n 2a - 2n
Volte: 110000/Ö3 110/√3 110/√3
Burden VA 100 200
Accuracy Class 3P 10
7 | بلخ | فاریاب | شیرین تگاب | 110KV Lighting arrester | Zinc Oxide surge Arrester ModelNO: ZLAX 25C SYSTEM NOM.DISCH CURRENT10 Kap PR.Reliefcurrent 40KA Rated voltage 96KV MCOV 76KV LD Class3 | Crompton Greaves limited | Nos | 3
8 | كابل | كابل | چمتله | ریلی محافظوی دیجیتل IDMT 3 O/C Relay -50/51 | ریلی محافظوی دیجیتل IDMT 3 O/C -Relay -50/51 ( شارتی O/C و اضافه باری O/L که هردو خاصیت را داشته باشد برای فیدر های 20 کیلوولت Invers Time Over Current Relay with inst. Hi set current Rate -1A, DC & AC supply range 5- , 185-250ACو DC175- 250V | JVS Electric (India) | Nos | 6
9 | پروان | پروان | پشته سرخ | Outgoing Feeder Circuit breaker | Out going Swich 20KV بامشخصات: VOLTAGE 24KV , SYM BREAKING CAPACITY 12.5KA,50HZ, NORMAL CURRENT 1250A ,MAKING CAPACITY 31.25KAP ,Short time current 12.5KA DURATION 3S. , P.F. Withstand 50kv , Impulse Withstand 125kvp , shunt trip coil 220V , SPRING Rel. coil 220V , INTERRUPTER BEL-VS30027 , TYPE VM36 , SPEC IS13118 , DIVISION BHOPAL | BHEL(INDIA) | سیت( مكلمل با ميكانيؤم أن) | 1
10 | پروان | پروان | پشته سرخ | Incoming Feeder Circuit breaker | Incoming Swich 20KV بامشخصات: VOLTAGE 24KV , SYM BREAKING CAPACITY 12.5KA,50HZ, NORMAL CURRENT 1250A ,MAKING CAPACITY 31.25KAP ,Short time curent 12.5KA DURATION 3S. , P.F. Withstand 50kv , Impulse Withstand 125kvp , shunt trip coil 220V , SPRING Rel. coil 220V , INTERRUPTER BEL-VS30027 , TYPE VM36 , SPEC IS13118 , DIVISION BHOPAL , YEAR 2013 | BHEL(INDIA) | سيت( مكمل با ميكانيؤم أن) | 1
11 | پروان | پروان | پشته سرخ | Current Transformer 220kV | CUURENT TARANSFORMER : Standard: IS 2705, Highest System Voltage: 245kV,, Insulation Level Kv/Kvp 460/1050, Frequency: 50Hz, Short Time current: 40kA for 1 sec, Rated Primary Current: 1600A, Extended Current Amps: 120%, CT Suitable Above MS: 1800MTRS, Ratio: 800-1600/1A, Core: 5, Burden: 20VA, Class: 0.2S ISF<5, Manufacturer's type Designation: Outdoor Oil filled CT | BHEL(INDIA) | Nos | 1
12 | پروان | پروان | پشته سرخ | Capacitor Voltage Transformer 220kV | Capacitor Voltage Transformer: Primary Voltage 220000/√3 , TYPE OUT DOOR , SECY TERMINAL 1a-1n, 1a-1n ,2a-2n,2a-2n ,3a-3n ,3a-3n, secy volt 110/√3,110/√3,110/√3, rated Burden (VA) 50 50 50 ,CLASS 3P 3P 0.2 , HZ 48-51 49.5-50.5 , TOTAL SIMULTANEOUS BURDEN 100VA , C2: 40333PF , C1: 4939PF , CN 4400pF, HIGHETS SYSTEM VOLTAGE 245KV, RATED VOLTAGE FACTOR/TIME 1.2/CONT. 1.5/30 SEC, INSULATION LEVEL KVP507/1158 , ELEC SPES: NO 610478, O .G .A . DRAWING NO. 34900000174 , SERIAL NO 6186394 | BHEL(INDIA) | Nos | 1
13 | پروان | پروان | پشته سرخ | Circuit Breaker 220kV | Circuit Breaker: ،Type: 200-SFM-40S, RATED VOLTAGE 245KV, RATED LINE CHARGING BREAKING CURRENT:1250A,MOTOR VOLTAGE 240VAC,RATED LIGHTNING IMPULSE WITHSTAND VOLTAGE 1175KVP,RATED SHORT·CIRCUIT BREAKING CURRENT 40KA, RATED DURATION OF SHORT CIRCUIT CURRENT 40KA/3SECS , RATED NORMAL CURRENT 1250A,RATED CLOSING VOLTAGE 220V.DC,,RATED OPERATING VOLTAGE 220V.DC , RATED SF6 GAS PRESSURE 8Kg/Cm².g(AT 20°C),RATED OPERATING SEQUENCE 0-0.3S-CO-3MIN-CO,STD-IEC 62271 - 100 , First pole to clear factor 1.3 , Type : 200-sfm.40s , Rated voltage and frequency for aux circuit 1ø, 240VAC, 50HZ, Total wt. with gas 3900kg , Gas wt. 24kg , CUSTOMER : BHEL | Crompton Greaves limited | سیت (یک عدد پُل با یک پایه میکانیزم ) | 1
14 | پروان | پروان | پشته سرخ | REF PROTECTION Relay | Type: P141, vx 110-250 , 100-240 V AC , Vn= 110-120 VAC , In=1/5 A, 50/60 Hz f | Schneider Electric (Micom) | Nos | 1
15 | پروان | پروان | پشته سرخ | DISTANCE PROTECTION( REL 670) | REL 670 , LINE DISTANCE PROTECTION LED , SERIAL NO : I1308011 , ORDER: 4200668667-010 , Ur , Ir as indicated , fr=50/60 HZ EL = 90 - 250VDC , YN1M251400 - PI , RL=220VDC , IR=5A , 5452/4210066231-BHEL 3000298563, X401 6I+ 6U 1,2 5A 3,4 5A 5,6 5A 7,8 5A 9,10 5A 11,12 5A 13,14 110 -220V 15,16 110-220V 17,18 110 -220V 19,20 110 - 220V 21,22 110 - 220V 23,24 110 - 220V | ABB (Indai) | Nos | 1
16 | پروان | پروان | پشته سرخ | RECTIFIER | Type :SINGLE FLOAT CUM BOOST - CP-CC 220V/40A-50A, EQUIPMENT: SINGLE FCB , INPUT : 415V/10% 50HZ±5% 3PH 4 WIRE AC SUPPLY,RATING : 220/50-40A,OUTPUT : CP 244±1%CC 296 CP 50A CC 40±2% | CHHABI ELECTRICALS PRIVATE LIMITED | سیت | 1
17 | کندهار | هلمند | دوراهی | SF6 Circuit Breaker | Type: 120 - SFM - 32B Rated Voltage: 145KV, Rated Current: 1600A, Rated Short Circuit: 40KA, Rated Frequncy : 50 HZ, , Rated Short Time Current: 40KA for 1 seconds | Crompton Greaves limited | سیت( سه فاز با میکانیزم ) | 1
18 | کندهار | هلمند | دوراهی | Sel-451-protection automation control relay | Power Supply: 125/250V , 120/230V, Frequncy:50/60HZ, POWER: 35W | Sel | Nos | 2
19 | کندهار | هلمند | دوراهی | D60-line distance protection system relay | Ratings: Control Power:125-250V, 0.7A/100 , 50/60HZ ,0.7A, Contact Inputs: 300V, Max 10mA | Sel | Nos | 2
20 | کندهار | هلمند | دوراهی | CVT For 110kv | Type: CVE 145 / 650 / 50, STD: IEC 60044-5(2004), HSV: 123kV, Freq: 50Hz, Insulation level: 230kV / 550 kVp, Equi.Capacitance:6000+10%, -5%pF , Volts: | Crompton Greaves limited | Nos | 2
A - NHF 1a - 1n 2a - 2n
Volts: 110000/√3 100/ √3 100/ √3
VA / Class -- / -- 10 / 0.5 3P 25 / 0.5 3P
21 | کندز | بغلان | گزه گیل | 220kV Current Transformer | core1:800-1600/1,CLps,V=800VRc=4 ohms Ie<50mA | BHEL | Nos | 1
core2:800-1600/1,CLps,V=800VRc=4 ohms Ie<50mA
core3:800-1600/1,CL0.2s,1sf<5
core4:800-1600/1,CLps,V=800VRc=4 ohms Ie<50mA
core5:800-1600/1,CLps,V=800VRc=4 ohms Ie<50mA
freqency-50HZ
Voltage(KVp) -245kv
1600AMPS
100KAP
40Ka for 1 second
قیمت مجموعی تجهیزات مورد نیاز سب ستیشن ها - لات پنجم | [9 empty] | 0
تذکر: کمپنی قراردادی دواطلب مکلف است تا به هزینۀ شخصی خویش ساحه را قبل از تهیه اجناس مندرج در جدول فوق را از نزدیک مشاهده نموده و از نحوه فعالیت، کارکرد و مشخصات کامل تجهیزات خود را مطمئن سازد.
|  |  | مدیریت حفظ و مراقبت سب ستیشن ها |  |  |  | معاونیت عملیاتی